Edwards Accelerator Lab

Monthly Fire Extinguisher Inspection

Due to the unpredictable accessibility and training requirements at Edwards Accelerator Lab the monthly inspection of the 29 fire extinguishers, 8 emergency lights, and 4 Wi-Fi phones in the facility will be conducted by Accelerator Personnel using the following inspection guidelines:

- Locate the inspection item, and circle Y on the inspection sheet.

- For fire extinguishers:

  - See that access to the extinguisher is not obstructed.

  - Verify that the seal securing the pin is intact.

  - Check nozzle to see that it is not obstructed.

  - Check that the annual inspection date is within the last year.

  - If any of the above is not true, DO NOT initial tag, and report to Facilities Management.

  - Otherwise, initial and date extinguisher tag.

  - Place check mark in notes column.

- For emergency lights:

  - Press and hold the test button for 3 seconds and be sure that lights illuminate and stay illuminated.

  - If lights do not work, note on inspection sheet, and notify accelerator engineer.

  - Place check mark in notes column.

- For phones:

  - Remove phone from base.  Screen should turn on.

  - Press up button once to show menu.

  - Press select button to select Missed Calls.

  - Press left soft key to clear missed calls.

  - Return phone to base.

  - If the phone does not work, note on inspection sheet, and notify accelerator engineer.

  - Otherwise, place check mark in notes column.

When inspection is finished, scan and email a copy of the inspection sheet to EHS.